## Slide 1: Neutrino Factory Mercury Flow Loop
V. Graves C. Caldwell
IDS-NF Videoconference
March 9, 2010

## Slide 2: Flow Loop Review
1 cm dia nozzle, 20 m/s jet requires 1.57 liter/sec mercury flow (94.2 liter/min, 24.9 gpm).
MERIT experiment showed that a pump discharge pressure of ~40 bar gauge required to produce the desired jet.
  Reference: SNS nominal flow 1440 liter/min (380 gpm), 7 bar gauge pump discharge pressure, ~1400 liters total Hg inventory
Basic flow scheme
  Pump → Nozzle → Jet/Beam Dump → Heat Exchanger → Pump

## Slide 3: Hg Flow
Minimize pressure drops through piping by increasing diameter
  2" nozzle supply piping transitioning to 1 cm nozzle
Actual NF Hg inventory may reach SNS volumes
  ~500 liters in the half-length beam dump shown
Overflow Mercury Drain
Mercury Pump
Gravity Drain Flow Control Valve
Storage Tank
Heat Exchanger
Beam Dump

## Slide 4: Gravity Drain Requires Flow Control
Bulk flow exits dump via overflow drains
Gravity drain intended to remain closed until end-of run, but this liquid becomes static
Decay heating requires gravity drain to have flow control
Mercury Jet
Proton Beam
Mercury Overflow
Gravity Drain Flow Control
Overflow drains
WC Shielding

## Slide 5: Target Building
Based on Study 2 concept
Mercury loop "hot cell" will probably extend into magnet chase
  Could require double containment of mercury
  Chase will certainly have a drain back into hot cell
Decay Channel Cryostats
Core Vessel
Mercury Process Hot Cell
Main Cryostat (Target Region)

## Slide 6: Heat Removal
From Study 2, the mercury jet/pool receive < 10% of beam energy; bulk goes into WC shielding
  Currently assumed to be WC spheres cooled by water
  Much larger heat exchanger needed to cool shielding
Considering that both W and WC must be water-cooled, their effective densities will approach that of Hg.
Consequently, IF a Hg target is selected, the infrastructure will be in place to support use of Hg as a solenoid shield.
  Would probably be a separate loop due to vastly different flow/pressure requirements, but could share a storage tank
Element/Compound | Density (g/cm^3)
Hg | 13.5
W | 19.3
WC | 15.8

## Slide 7: Future Work
  Continue development of Target Building infrastructure conceptual design
  Look further into the mechanics of the region upstream of the nozzle
    Remote maintenance / assembly / disassembly
    Mercury flow